How to program a CIP Generic Explicit Message with ControlLogix revision 10 or 11 Firmware that uses an Attribute ID of zero.

Starting with Revision 10 of ControlLogix Processor Firmware, sending a CIP Explicit MSG to a device will not send the Attribute byte if the Attribute ID value is zero.  Using an Attribute ID of zero is valid with some Class ID’s.

This is a change of operation from the way that the same MSG command would operate in previous versions of Firmware.

To resolve the issue, use the following steps as a work around:

- Create an array of data type SINT   (Byte)

- Create a Ladder Instruction that copies the current Data Source tag into the array of SINT's.

The destination element of the COPY instruction is element 1, leaving element 0 set to zero (which

will be sent as the Attribute Field by the MSG command.)

- Modify the Source Field of the MSG command to use the array created in Step 1.

Here is a sample logic file that uses this method:

Rung 1 was added to copy the original data_source for the MSG instruction to element 1 of the array of SINT's. Remember element 0 must be set to Zero.

In essence, we’re shifting all data by a byte leaving a byte with a value of zero in the first element of the Single Integer Array.

Original Source		     New Data

(Byte) 			     (Byte)

| 8 (1st Data Byte) |  | 0 (Attribute ID) |
| --- | --- | --- |
| 0 |  | 8 (1st Data Byte) |
| 9 |  | 0 |
| 0 |  | 9 |
| 10 |  | 0 |
| 0 |  | 10 |
|  |  | 0 |

Here is the MSG instruction:

Here’s the original Source Data array:

Here's the new SINT array:

Note: The 1st element is a zero.  This value represents the Attribute Field.  All data that follows is the data that will be sent as part of the Explicit MSG.  parameter information request.

Here are the values in the Destination Tag specified in the MSG:

(They contain the results back from the Explicit MSG)